## Usages
building_function | lighting_per_area_w_per_m2 | lighting_fraction_radiant | occupancy_per_area_people_per_m2 | occupant_sensible_heat_gain_w_per_m2 | occupant_latent_heat_gain_w_per_m2 | water_heater_w_per_m2 | service_water_heating_peak_flow_per_area | water_heater_fraction_lost | service_water_heating_target_temperature | ventilation_air_changes | ventilation_per_area | ventilation_per_person | electric_equipment_per_area_w_per_m2 | electric_equipment_fraction_radiant | electric_equipment_fraction_latent | electric_equipment_fraction_lost | refrigerator | refrigerator_fraction_radiant | refrigerator_fraction_latent | refrigerator_fraction_lost | freezer | freezer_fraction_radiant | freezer_fraction_latent | freezer_fraction_lost | dishwasher | dishwasher_fraction_radiant | dishwasher_fraction_latent | dishwasher_fraction_lost | oven | oven_fraction_radiant | oven_fraction_latent | oven_fraction_lost | washer | washer_fraction_radiant | washer_fraction_latent | washer_fraction_lost | dryer | dryer_fraction_radiant | dryer_fraction_latent | dryer_fraction_lost
Automotive facility | 8.6031 | 0.5 | 0.050018 |  |  |  | 0.02273 |  | 60 | 0 | 1.5 | 0 | 5.0018 | 0.5 | 0 | 0
Convention centre | 10.904 | 0.5 | 0.12505 |  |  |  | 0.018942 |  | 60 | 0 | 0 | 15 | 2.5009 | 0.5 | 0 | 0
Courthouse | 10.904 | 0.5 | 0.066691 |  |  |  | 0.020204 |  | 60 | 0 | 0 | 15 | 5.0018 | 0.5 | 0 | 0
Dining - bar lounge/leisure | 10.904 | 0.5 | 0.10004 |  |  |  | 0.058088 |  | 60 | 0 | 0 | 30 | 1.0004 | 0.5 | 0 | 0
Dining - cafeteria/fast food | 9.7035 | 0.5 | 0.10004 |  |  |  | 0.058088 |  | 60 | 0 | 0 | 20 | 1.0004 | 0.5 | 0 | 0
Dining - family | 10.2037 | 0.5 | 0.10004 |  |  |  | 0.058088 |  | 60 | 0 | 0 | 20 | 1.0004 | 0.5 | 0 | 0
Dormitory | 6.1022 | 0.5 | 0.033345 |  |  |  | 0.084185 |  | 60 | 0 | 0 | 15 | 2.5009 | 0.5 | 0 | 0
Exercise centre | 9.0033 | 0.5 | 0.10004 |  |  |  | 0.04546 |  | 60 | 0 | 0 | 25 | 1.0004 | 0.5 | 0 | 0
Fire station | 7.2026 | 0.5 | 0.040015 |  |  |  | 0.080817 |  | 60 | 0 | 1.5 | 0 | 2.5009 | 0.5 | 0 | 0
Gymnasium | 10.1037 | 0.5 | 0.10004 |  |  |  | 0.04546 |  | 60 | 0 | 0 | 25 | 1.0004 | 0.5 | 0 | 0
Health care clinic | 9.7035 | 0.5 | 0.050018 |  |  |  | 0.02273 |  | 60 | 0 | 0 | 15 | 7.5027 | 0.5 | 0 | 0
Hospital | 11.3041 | 0.5 | 0.050018 |  |  |  | 0.02273 |  | 60 | 0 | 0 | 15 | 7.5027 | 0.5 | 0 | 0
Hotel/Motel | 9.4034 | 0.5 | 0.040015 |  |  |  | 0.10102 |  | 60 | 0 | 0.091 | 0 | 2.5009 | 0.5 | 0 | 0
Library | 12.8047 | 0.5 | 0.050018 |  |  |  | 0.02273 |  | 60 | 0 | 0 | 15 | 2.5009 | 0.5 | 0 | 0
Long-term care - dwelling units | 5.502 | 0.5 | 0.040015 |  |  |  | 0.10102 |  | 60 | 0 | 0.06 | 5 | 1.5005 | 0.5 | 0 | 0
Long-term care - other | 5.502 | 0.5 | 0.040015 |  |  |  | 0.10102 |  | 60 | 0 | 0.06 | 5 | 1.5005 | 0.5 | 0 | 0
Manufacturing facility | 12.6046 | 0.5 | 0.033345 |  |  |  | 0.015153 |  | 60 | 0 | 1.5 | 0 | 10.0036 | 0.5 | 0 | 0
Motion picture theatre | 8.203 | 0.5 | 0.12505 |  |  |  | 0.018942 |  | 60 | 0 | 0 | 15 | 1.0004 | 0.5 | 0 | 0
Museum | 11.004 | 0.5 | 0.050018 |  |  |  | 0.015153 |  | 60 | 0 | 0 | 20 | 2.5009 | 0.5 | 0 | 0
Office | 8.8032 | 0.5 | 0.040015 |  |  |  | 0.018184 |  | 60 | 0 | 0 | 20 | 7.5027 | 0.5 | 0 | 0
Penitentiary | 8.7032 | 0.5 | 0.033345 |  |  |  | 0.067348 |  | 60 | 0 | 0 | 20 | 2.5009 | 0.5 | 0 | 0
Performing arts theatre | 14.9054 | 0.5 | 0.12505 |  |  |  | 0.018942 |  | 60 | 0 | 0 | 15 | 1.0004 | 0.5 | 0 | 0
Police station | 9.4034 | 0.5 | 0.040015 |  |  |  | 0.018184 |  | 60 | 0 | 0 | 15 | 7.5027 | 0.5 | 0 | 0
Post office | 9.4034 | 0.5 | 0.040015 |  |  |  | 0.018184 |  | 60 | 0 | 0 | 15 | 7.5027 | 0.5 | 0 | 0
Religious building | 10.8039 | 0.5 | 0.20007 |  |  |  | 0.015153 |  | 60 | 0 | 0 | 15 | 1.0004 | 0.5 | 0 | 0
Retail area | 13.5049 | 0.5 | 0.033345 |  |  |  | 0.0067348 |  | 60 | 0 | 0.3 | 0 | 2.5009 | 0.5 | 0 | 0
School/university | 9.4034 | 0.5 | 0.12505 |  |  |  | 0.037883 |  | 60 | 0 | 0 | 15 | 5.0018 | 0.5 | 0 | 0
Sports arena | 9.8036 | 0.5 | 0.10004 |  |  |  | 0.04546 |  | 60 | 0 | 0 | 15 | 1.0004 | 0.5 | 0 | 0
Storage garage | 2.3008 | 0.5 | 0.0010004 |  |  |  | 0 |  | 60 | 0 | 1.5 | 0 | 0 | 0.5 | 0 | 0
Town hall | 9.6035 | 0.5 | 0.040015 |  |  |  | 0.018184 |  | 60 | 0 | 0 | 15 | 7.5027 | 0.5 | 0 | 0
Transportation facility | 7.5027 | 0.5 | 0.066691 |  |  |  | 0.021888 |  | 60 | 0 | 0 | 15 | 1.0004 | 0.5 | 0 | 0
Warehouse | 7.1026 | 0.5 | 0.00066691 |  |  |  | 0.0010102 |  | 60 | 0 | 0.05 | 0 | 1.0004 | 0.5 | 0 | 0
Workshop | 12.8047 | 0.5 | 0.033345 |  |  |  | 0.015153 |  | 60 | 0 | 0 | 20 | 10.0036 | 0.5 | 0 | 0
single family house | 5.5 | 0.4 | 0.04 |  |  | 0 | 0.1 | 0.8 | 60 | 0 | 0.06 | 0 | 5 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0.8
MURB | 5.5 | 0.4 | 0.04 |  |  | 0 | 0.1 | 0.8 | 60 | 0 | 0.06 | 0 | 5 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0.8
duplex | 5.5 | 0.4 | 0.04 |  |  | 0 | 0.1 | 0.8 | 60 | 0 | 0.06 | 0 | 5 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0.8
triplex | 5.5 | 0.4 | 0.04 |  |  | 0 | 0.1 | 0.8 | 60 | 0 | 0.06 | 0 | 5 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0 | 0.8 | 0.2 | 0 | 0.3 | 0.8 | 0.2 | 0 | 0.8