DOE NEUP FY 2026 – CINR Pre‑Application Technical Volume
Topic Area 11: Licensing, Safety, and Security

Digital Twins for Safe, Reliable, and Cybersecure Remote Operation of Microreactors

Principal Investigator: William Charlton, University of Texas at Austin

Subrecipients: Andrew Hahn SNL, Somebody, INL

Period: 36 months

DOE Request: $1,000,000

# Problem Statement and Mission Relevance

The economic viability of microreactors depends in part on safely reducing on-site staffing requirements, including the ability to operate multiple reactors from remote locations [1]. To ensure that remotely operated microreactors remain both reliable and cybersecure, remote instrumentation and control (I&C) architectures must be developed, evaluated, and validated prior to deployment. One promising approach is the use of digital twins (DTs). A digital twin is a digital representation of a physical system in which data flow bidirectionally between the digital and physical twins, with both integrating the available data. When applied to remote operations, digital twins can be used to verify instrumentation signals, validate control commands, and detect anomalous behavior in data streams that may indicate cyber intrusion.

This project will develop and experimentally deploy, on a 1-MW research reactor, multiple candidate remote-operation architectures, including the Digital Twin Certification System (DTCS), single-DT anomaly detection systems, traditional encryption-based approaches, and other concepts. The cybersecurity and operational performance of these architectures will be evaluated using existing hardware and infrastructure at the TRIGA reactor at the University of Texas (UT) at Austin, providing a controlled but realistic testbed for remote nuclear operations. This work will constitute the first experimental demonstration of DTCS on an operating nuclear reactor, enabling a direct comparison of performance, resource requirements, and cybersecurity effectiveness across alternative architectures. Results will be explicitly mapped to existing Nuclear Regulatory Commission (NRC) and other cybersecurity standards to assess licensing relevance and regulatory implications.

This project builds on ongoing research under the Texas Digital Twin Nuclear Reactor Program funded by the State of Texas. It directly addresses NEUP Topic Area 11 by developing and experimentally demonstrating cybersecure remote operation concepts that reduce regulatory uncertainty and support licensing-relevant decision-making for advanced reactors.

# 2. State of the Art and Technical Innovation

Research in the cybersecurity of nuclear systems and the use of digital twins in enabling their security has expanded rapidly in recent years, driven by the increasing complexity of digital instrumentation and control (DI&C) systems and the economic case for remote reactor operation. As these systems become more complex and our ability to simulate them becomes more comprehensive due to the exponential increase in cloud compute capacity, integrating DTs into these systems to increase safety and security becomes an obvious solution.

On the regulatory side, efforts such as IEC 62645 have mapped nuclear-specific cybersecurity requirements onto broader ISO/IEC and NIST guidance [11], [12], [13], [14]. The NRC has also published forward-looking reports anticipating that semi-automated and remotely operated advanced reactors will soon require regulatory treatment [3]. Work by national laboratories, including Sandia National Laboratories (SNL) and

Figure 1 - Diagram of DTCS architecture as applied to a remotely operated microreactor [4]

Idaho National Laboratory (INL), has emphasized the importance of performance-based regulation, risk-informed decision making, and the potential adoption of trust-based or zero-trust architectures for operational technology environments [2], [15]. Computational and simulation work to build and test these kinds of systems has progressed in parallel. SNL has developed the ARCADE framework to simulate cyberattacks on nuclear systems [16], while INL has built DT for the multiple research reactors to support remote operation studies [17].

The DTCS, as originally described by Stevens [4], [5], and shown in Figure 1, makes remote operation more secure by establishing a certification process in which digital twins running at both the reactor and the control room independently predict system behavior. Commands and sensor data are only accepted when the predicted values from these twins match the measured or reported system states within predefined tolerances. This mutual verification framework ensures that both operational commands and diagnostic signals are validated against trusted models, making it significantly harder for cyber-intrusion to inject false data or manipulate control actions undetected.

Our proposed innovation is the creation of a first-of-a-kind experimental testbed for the DTCS on an operating nuclear reactor, enabling direct benchmarking of its performance and cybersecurity effectiveness against alternative remote-operation architectures. This testbed is enabled by the development at UT Austin of a low-worth aluminum control rod that will be installed as an experimental component in the UT TRIGA reactor. The control rod is designed to smooth reactor power fluctuations and, while power-affecting, is a non-safety-related structure, system, or component (SSC), allowing it to be operated as a reactor experiment under controlled conditions.

This configuration creates a unique and previously unavailable opportunity to prototype and evaluate remote operation technologies under realistic nuclear operating conditions without compromising reactor safety. To date, aside from NRC-mandated emergency shutdown panels (i.e. under Code of Federal Regulations 10 CFR 50.48 [12]), remote control of power-affecting devices has not been implemented or experimentally evaluated at an operating nuclear reactor (to the knowledge of the authors). The proposed testbed therefore represents a significant advance, providing regulator-relevant evidence on the feasibility, performance, and cybersecurity implications of digitally mediated remote control in nuclear systems.

Alongside DTCS, the project will remain open to exploring other DT-based security architectures and data security techniques such as obfuscation techniques (e.g., Directed Infusion of Data (DIOD)  [6], [7]) and anomaly-detecting DTs [8], [9], [10]. Together, these approaches represent a broad solution space of DT configurations and data security techniques that could be deployed to secure remote operations. These range from high-fidelity physics-based models to lightweight reduced-order or machine-learning backed twins, each with tradeoffs in computational speed, accuracy, and resource requirements. How such heterogeneous DTs should be combined and validated to maximize system integrity remains an unresolved research question.

# 3. Technical Approach

This project will design and demonstrate a set of DT-enabled remote operation architectures, primarily DTCS, for the aluminum smoothing rod to be installed at the UT TRIGA, building on the ongoing research under the Texas Digital Twin Nuclear Reactor Program funded by the State of Texas. The demonstrations will explicitly test the systems against man-in-the-middle (MitM) attacks, compromised DT scenarios, malicious operator commands, and failed sensors. The resulting architectures will be mapped to existing regulatory frameworks to illustrate how DT-based cybersecurity systems can meet or exceed regulatory cybersecurity controls for nuclear facilities.

Task 1 will leverage existing physics-based and data-driven DTs the UT TRIGA developed by UT [9], [10]. These will be configured as real-time predictive systems for certification of commands and sensor data. The work will explore tradeoffs between fidelity, speed, computational cost, and prediction horizon. Multiple DT systems may be deployed in parallel, for example, running a fast DT with a shorter prediction horizon to enable a more complex, higher fidelity DT with a longer prediction horizon to run without slowing down operations. This work will use the application of a DTCS system as a framework to continue the development of a refined toolbox of digital twins, each adapted to perform well in a specific metric. These DTs can be comprehensively combined to certifying secure communication between remote monitoring and operating stations.

Our reduced-order models can be tuned to run extremely quickly [9], allowing them to provide an initial check that a proposed control action will not cause any immediate unsafe or undesirable outcomes. In this way, the reduced-order DTs act as a rapid screening tool, with the higher-fidelity DTs serving as the authoritative certifiers of long-term safety. Seo's work on integrating sensor data to constantly improve DTs can be utilized to tune DTs used for assistance in the operation of the specific reactor being controlled, resulting in improved performance [10].

Task 2 will focus on building a certifier to compare outputs of the multiple DTs to ensure that commands and data sent to and from the reactor have not been modified. Note that in Stevens's work [4,5] the certifier was not a primary subject and was not optimized. Thresholds for acceptable DT error will be established through analysis of the regions of optimal operation. The certifier logic will be designed to flag divergences and initiate predetermined optimal-state transitions.

More specifically, different criteria for identifying when unsafe commands, or altered commands, have been sent will be evaluated and tested on a simulated system before being implemented into the physical system. For example, it is not immediately clear how predicted outputs from the certifying DTs should be compared to determine if their input has been modified. Candidates for flagging criteria to determine altered commands or data could be total weighted state error, single term error, or percent error between the predictions. When the certifier has access to multiple DT certifier systems, if the predicted error is high enough, the certifier could be programmed to request that higher fidelity DTs be run before it will certify the commands. This solution space offers a multitude of variables to optimize for, and experimental testing will be crucial to solving.

Task 3 will integrate the DTCS-secured architecture with the existing UT TRIGA infrastructure. Existing data pipelines will be used as a foundation for monitoring. The specific control hardware of the low-worth

Table 1 - Gantt chart of tasks

|  |  | FY27 |  |  |  | FY28 |  |  |  | FY29 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 | Q1 | Q2 | Q3 | Q4 |
| Task 0 | Management & Reporting |  |  |  |  |  |  |  |  |  |  |  |  |
| Task 1 | Leverage Existing DTs |  |  |  |  |  |  |  |  |  |  |  |  |
| Task 2 | DT Certifier System |  |  |  |  |  |  |  |  |  |  |  |  |
| Task 3 | DTCS Demonstration |  |  |  |  |  |  |  |  |  |  |  |  |
| Task 4 | Performance Benchmarking |  |  |  |  |  |  |  |  |  |  |  |  |

aluminum control rod will be integrated to be commanded remotely. To simulate what a level-4 autonomous reactor looks like [18], the low-worth control rod will run mostly autonomously to smooth the power of the reactor using a relatively simple PID control scheme. Commands sent to the controls system will command the rod to change its control scheme variables, such as set point or gain, to shape the reactor power differently. This emulates a remote operator requesting a microreactor to change its operational mode, for example, from steady power production to load following. DTCS and alternative DT-based verification methods will be applied before any control commands are executed. For comparison, single, locally hosted DT systems will also be tested against DTCS.

Task 4 will benchmark system performance in terms of latency, accuracy, computational resource requirements, and false positives. Explicit tests will be conducted against a variety of threat scenarios, including man-in-the-middle (MitM) attacks, compromised DTs on either end of the link, malicious operator commands, and failed or unreliable sensors. The goal is to demonstrate that DT-enabled architectures can detect these threats and automatically bring the reactor to a safe state.

# 4. Scope of Work

Throughout all tasks, the project will map the implemented controls against NIST SP 800-53/800-82 High, NRC RG 5.71, NEI 08-09, and IEC 62645/62859/63096 [11], [12], [13], [14]. The analysis will identify which required controls are inherently satisfied by DTCS and other DT-based verification methods and highlight the remaining controls that must be implemented outside of a DTCS or other DT verification system.  This kind of analysis is critical to highlighting the importance of these systems but is difficult to perform because the NRC, which acts as the primary body for these regulations, is currently in the process of determining exactly what will be required of remotely operated reactors.

Table 1 presents the project schedule in the form of a Gantt chart spanning three fiscal years (FY27 through FY29). The schedule is structured to deliberately overlap modeling, system development, and experimental activities to reduce technical risk and enable early feedback between tasks. This phased yet overlapping structure ensures that lessons learned during early modeling and design directly inform physical implementation and validation, while maintaining schedule flexibility to address emergent technical or regulatory insights.

# 5. Expected Outcomes and Impact

This project will produce a regulator-aligned demonstration of DTCS applied to remote reactor operation, along with a comparative evaluation of DTCS against alternative DT-based cybersecurity architectures such as single anomaly-detecting DTs. We will deliver a proof-of-concept for dual DTs operating in certification roles on either end of a remote operation link, supported by experimental validation against cyberattacks and system failures. Finally, the work will provide a traceable mapping of DT-based cybersecurity architectures to existing and possible future regulatory frameworks, supporting adoption by advanced reactor developers and operators.

Bibliography
[1] H. C. Bryan, K. W. Jesse, C. A. Miller, and J. M. Browning, “Remote Nuclear Microreactors: A Preliminary Economic Evaluation of Digital Twins and Centralized Offsite Control,” Frontiers in Nuclear Engineering, vol. 2, Dec. 2023, Article 1293908, https://doi.org/10.3389/fnuen.2023.1293908.

[2] R. Fasano, A. Hahn, J. James, C. Lamb, and A. Haddad, Cyber‑Physical Risks for Advanced Reactors, Sandia National Laboratories, Albuquerque, NM, SAND2021‑11995, Sept. 2021, https://doi.org/10.2172/1854721.

[3] T. Rivera and I. Garcia, NRC Regulatory Efforts for Cybersecurity of Advanced Reactors, U.S. Nuclear Regulatory Commission, Washington, DC.
[4] K. Stevens, Digital Twin Model Development for a Proof‑of‑Concept Study of a Novel Remote Monitoring and Operation Framework for Nuclear Microreactors, Ph.D. dissertation, Oregon State University, Corvallis, OR, June 2024.
[5] K. Stevens et al., “Digital Twin Framework for the Resilient Remote Monitoring and Operation of Nuclear Microreactors,” Proceedings of the AHFE International Conference, 2023, https://doi.org/10.54941/ahfe1004400.

[6] T. Lewis and H. S. Abdel‑Khalik, “On the Control of Nonlinear Systems Using Directed Infusion of Data (DIOD),” unpublished technical manuscript.
[7] C. Lamb and D. Sandoval, Barriers and Alternatives to Encryption in Critical Nuclear Systems, Sandia National Laboratories, Albuquerque, NM, SAND2023‑09883, Oct. 2023, https://doi.org/10.2172/2430264.
[8] Y. Zhang, C. Du, Z. Chen, Z. Feng, and W. Gui, “Digital Twin‑Based Resilient Model Predictive Control for Industrial Cyber‑Physical Systems,” IEEE Journal of Emerging and Selected Topics in Industrial Electronics, 2025, https://doi.org/10.1109/JESTIE.2025.3528881.
[9] J. Ross, B. Collins, C. Gentry, and K. Clarno, “A Multiphysics Reduced‑Order Model for TRIGA Reactors Using Dynamic Mode Decomposition,” submitted to Mathematics and Computation (M&C 2025).
[10] J. Seo and W. S. Charlton, “Technical Challenges and Gaps in Integration of Advanced Sensors, Instrumentation, and Communication Technologies with Digital Twins for Nuclear Applications,” Proceedings of the 13th NPIC&HMIT Conference, Knoxville, TN, American Nuclear Society, 2023, pp. 710–719, https://doi.org/10.13182/NPICHMIT23‑41192.
[11] I. Garcia and T. Rivera, Draft Regulatory Guide DG‑5075, U.S. Nuclear Regulatory Commission, Washington, DC.
[12] U.S. Nuclear Regulatory Commission, “Protection of Digital Computer and Communication Systems and Networks,” Title 10, Code of Federal Regulations, Part 73.54.
[13] T. Smith et al., The IEC Standard Series on Cybersecurity for I&C and Electrical Systems in Nuclear Power Plants, International Electrotechnical Commission, Geneva, Switzerland.
[14] K. Stouffer et al., Guide to Operational Technology (OT) Security, National Institute of Standards and Technology, Gaithersburg, MD, NIST Special Publication 800‑82 Rev. 3, Sept. 2023, https://doi.org/10.6028/NIST.SP.800‑82r3.
[15] B. Karch, R. Valme, M. Tanaka, and C. Lamb, Advanced Reactor Control Systems Authentication Methods and Recommendations, Sandia National Laboratories, Albuquerque, NM, SAND2023‑09882, Oct. 2023, https://doi.org/10.2172/2430252.
[16] A. S. Hahn et al., “Methods for Prioritizing Simulation of Unsafe Control Actions for Cybersecurity Analysis,” Sandia National Laboratories, Albuquerque, NM.
[17] R. Stewart et al., “The AGN‑201 Digital Twin: A Test Bed for Remotely Monitoring Nuclear Reactors,” Annals of Nuclear Energy, vol. 213, Apr. 2025, Article 111041, https://doi.org/10.1016/j.anucene.2024.111041.
[18] D. A. Kim, K. Lawson‑Jenkins, D. D. Eskins, I. Garcia, and T. Rivera, Cybersecurity Considerations of Autonomy in Nuclear Facilities (Cybersecurity Licensing Activities), U.S. Nuclear Regulatory Commission.